## Slide 1: Fire Damper process workbook
V1 DEC 2023

## Slide 2: A unique non-for-profit initiative comprising major contractors, specialist installers and relevant trade associations A collaborative forum to drive culture change through the design and construction process to improve fire safety in buildings Our mission is to improve the delivery of well designed, specified and installed passive fire protection by focusing on 3 key areas: Process, Testing and Education.

## Slide 3: Objective – FIRE DAMPERs
The objective of this presentation is to illustrate a best practice approach to the design and specification of Fire Dampers and their associated services penetration seals where they pass through fire compartment walls or floors.
The aim is to give the reader an understanding of the process required to ascertain the route to achieve an appropriate fire damper, compatibility of the fire wall or floor system and the access arrangements for installation, digital recording and future maintenance
The output of the process will produce the classification of the fire damper for selection.

## Slide 4
Fire Damper Work Book Example
Passive code

## Slide 5: The Process required for descriptive Fire Dampers
Example:
Refuge in protected corridor with supply air and extract.
Key Related Standards
BE EN 1366-2:2015 Fire resistance tests for service installations - Fire dampers
BS EN 1363-1:2020. Fire resistance tests. General requirements
BS EN 1364-1:2015. Fire resistance tests for non-loadbearing elements. Walls
BS EN 13501–3: Fire classification of construction products and building elements: fire resisting ducts and fire dampers
BS EN 15650: Ventilation for buildings – Fire dampers
BS EN 15882-2:2015 Extended application of results from fire resistance tests for service installations. Fire dampers
DW145 Installation of Fire and Smoke Dampers
TR19 Internal Cleanliness of Ventilation systems
Key Classifications
(E) – Integrity (I)– Insulation (S) – Low leakage
The mounting positions walls Ve or floors Ho
Test both ways for fire (i ↔ o)
Supporting Constructions – Rigid or Symmetrical Partition or other if TESTED.
Cycle tests - Additional optional classification
C10000 - 10000 operations for motorised (MFD) fire dampers only.
Notes: Paul to change images

## Slide 6
Gateways

## Slide 7
The Process required for descriptive Fire Dampers.
Its Complicated

## Slide 8
The Process required for descriptive Fire Dampers.
Simplification of the below flow diagram follows.
Building purpose group/fire safety space risk
System fire safety operational type. Static, Transient, Dynamic.
E120(ho i↔o )S - (300Pa)
classification for product fire safety type
Supporting construction compatibility type /P.F safety seal type
The installation/maintenance access types.
Simplify It!!!

## Slide 9
TECHNICAL Quality Assurance. Setting of the appropriate product for the circumstances. Any change is ‘major’ once this has been formulated.
* Culmination of all product types to verify the appropriate wall type.
**Building Regulations Functional Requirements, Approved Documents: Part L, O, F, B.

## Slide 10
**Design of system to components to meet all functional requirements of the Building Regulations
Operational type**. Building Regulations Functional Requirements, Approved Documents: Part L, O, F, B.
Part L. Evidence that the system energy performances are within the limits of the calculated performance.
Part O. Evidence that the system performance will prevent overheating where designed to do so.
Part F. Evidence that the system performance will supply reasonable levels of ventilation.
Part B. Evidence that the systems fire prevention devices do not impeded Parts, L, O, F and meet the space risk requirements

## Slide 11: * Culmination of all product types to verify the appropriate wall type. System approach
Flues
Pipes & Trays
Fire Dampers
Smoke Control Dampers
Fire Resistant Ducts Smoke extract ducts
Cable Encapsulation
Fire Curtains
Busbars
Wall Types
Fire Doors
Lift Doors

## Slide 12: The Process required for descriptive Fire Dampers
Establish the building fire safety purpose group type
Establish the building fire safety shape
Establish the building fire safety form
Establish the fire safety space risk types
Review lessons learned from previous projects
Establish the building passive fire safety review team
Gateway points
Building purpose group/fire safety space risk .
System fire safety operational type. Static, Transient, Dynamic.
Example:
Refuge in protected corridor with supply air and extract. Mark in blue.
Notes: Suggest zone in

## Slide 13: Building purpose group/fire safety space risk
Purpose Groups
1 a
2 a
2 b
1 b/c
3
4
5
6
7a
7b
Shape
Space Risks
Refuge
Smoke
Fire
Sleeping
Lighting
Power
Evac Type
Fire Fighting
Form & Space type
Notes: Paul to change images

## Slide 14: Building purpose group/fire safety space risk
Purpose Groups
1 a
2 a
2 b
1 b/c
3
4
5
6
7a
7b
Shape
Form & Space type
Space Risks
Refuge
Smoke
Fire
Sleeping
Lighting
Power
Evac Type
Fire Fighting
>+50m
>+18m
>+11m
-----
>-10m
<30m
<30m
Notes: Paul to change images

## Slide 15: The Process required for descriptive Fire Dampers
System fire safety operational type. Static, Transient, Dynamic.
Establish the passive fire systems operational types
Building purpose group/fire safety space risk
Gateway points
Establish the Passive fire safety time ratings
E120(ho i↔o )S - (300Pa)
classification for product fire safety type
Example:
Refuge in protected corridor with supply air and extract.
Notes: Paul to change images

## Slide 16: System fire safety operational type. Static, Transient, Dynamic.
Protected Corridor or Lobby
Sleeping, Clinical
Space Type
Risk
Phased Evacuation
Simultaneous Evacuation
Power Critical supplies
Fire Fighting
Time
Operation
30-120 minutes
Automatic activated to closed position by fire alarm activation
30-120 minutes
30-120 minutes
30-120 minutes
30-120 minutes
30-120 minutes
Automatic activated to closed position by fire alarm activation
Activated by fusible link at 72oc to closed position
Automatic activated to closed position by fire alarm activation
Automatic activated to closed position by fire alarm activation
Activated by fusible link at 72oc to closed position
Blade types DP (AD: L)
Power and Fire Signals
Power Supply. Fire Alarm Interface.
Power Supply. Fire Alarm Interface.
Power Supply. Fire Alarm Interface.
Power Supply. Fire Alarm Interface.
No requirement
No requirement
Smoke (S)
Fire (E)
Insulation (I)
Radiance (W)
Fusible Link Shutter
Single
blade
Opposed
blade
Parallel
Blade
Blade type must be chosen to ensure that the Part L Specific fan powers work
Ve – Vertical
Ho - Horizontal
Notes: Paul to change images

## Slide 17
Protected Corridor or Lobby
Sleeping, Clinical
Space Type
Risk
Phased Evacuation
Simultaneous Evacuation
Power Critical supplies
Fire Fighting
Time
Operation
30-120 minutes
Automatic activated to closed position by fire alarm activation
30-120 minutes
30-120 minutes
30-120 minutes
30-120 minutes
30-120 minutes
Automatic activated to closed position by fire alarm activation
Activated by fusible link at 72oc to closed position
Automatic activated to closed position by fire alarm activation
Automatic activated to closed position by fire alarm activation
Activated by fusible link at 72oc to closed position
Blade types DP (AD: L)
Power and Fire Signals
Power Supply. Fire Alarm Interface.
Power Supply. Fire Alarm Interface.
Power Supply. Fire Alarm Interface.
Power Supply. Fire Alarm Interface.
No requirement
No requirement
Smoke (S)
Fire (E)
Insulation (I)
Radiance (W)
Fusible Link Shutter
Single
blade
Opposed
blade
Parallel
Blade
Blade type must be chosen to ensure that the Part L Specific fan powers work
Ve – Vertical
Ho - Horizontal
System fire safety operational type. Static, Transient, Dynamic.
Notes: Paul to change images

## Slide 18: The Process required for descriptive Fire Dampers
E120(ho i↔o )S - (300Pa)
classification for product fire safety type
Establish the Passive fire safety classification types
Create the Passive fire safety systems Seal registers
Establish descriptive classification for product fire safety type
Gateway points
System fire safety operational type. Static, Transient, Dynamic.
Supporting construction compatibility type /P.F safety seal type
Example:
Refuge in protected corridor with supply air and extract.
Notes: Paul to change images

## Slide 19: Classification for product fire safety type
Protected Corridor or Lobby
Sleeping, Clinical
Space Type
Risk
Phased Evacuation
Simultaneous Evacuation
Power Critical supplies
Fire Fighting
Time
Operation
30-120
AD: B. Method 4
30-120
30-120
30-120
30-120
30-120
Blade types DP (AD: L)
Direction of Fire
Smoke (S)
Fire (E)
Insulation (I)
Radiance (W)
E.S
E.S
E.S
E.S
E
E
AD: B. Method 4
AD: B. Method 4
AD: B. Method 4
AD: B. Method 1
AD: B. Method 1
Fusible Link Shutter
Single
blade
Opposed
blade
Parallel
Blade
Blade type must be chosen to ensure that the Part L Specific fan powers work
(i ↔ o)
(i ↔ o)
(i ↔ o)
(i ↔ o)
(i ↔ o)
(i ↔ o)
Cycling
Up to C10000
Up to C10000
Up to C10000
Up to C10000
Ve – Vertical
Ho - Horizontal
Plane of Fire
Ve or Ho
Ve or Ho
Ve or Ho
Ve or Ho
Ve or Ho
Ve or Ho
Notes: Paul to change images

## Slide 20
Protected Corridor or Lobby
Sleeping, Clinical
Space Type
Risk
Phased Evacuation
Simultaneous Evacuation
Power Critical supplies
Fire Fighting
Time
Operation
30-120
AD: B. Method 4
30-120
30-120
30-120
30-120
30-120
Blade types DP (AD: L)
Direction of Fire
Smoke (S)
Fire (E)
Insulation (I)
Radiance (W)
E.S
E.S
E.S
E.S
E
E
AD: B. Method 4
AD: B. Method 4
AD: B. Method 4
AD: B. Method 1
AD: B. Method 1
Fusible Link Shutter
Single
blade
Opposed
blade
Parallel
Blade
Blade type must be chosen to ensure that the Part L Specific fan powers work
(i ↔ o)
(i ↔ o)
(i ↔ o)
(i ↔ o)
(i ↔ o)
(i ↔ o)
Cycling
Up to C10000
Up to C10000
Up to C10000
Up to C10000
Ve – Vertical
Ho - Horizontal
Plane of Fire
Ve or Ho
Ve or Ho
Ve or Ho
Ve or Ho
Ve or Ho
Ve or Ho
Classification for product fire safety type
Notes: Paul to change images

## Slide 21: The Process required for descriptive Fire Dampers
Supporting construction compatibility type /P.F safety seal type
Establish fire safety descriptive supporting construction compatibility type
Establish the passive fire safety seal descriptive type
E120(ho i↔o )S - (300Pa)
Gateway points
The installation/maintenance access types.
Example:
Refuge in protected corridor with supply air and extract.
classification for product fire safety type
Vertical Symmetrical Flexible – EN520
Vertical or Horizontal Rigid – Concrete/ Block > 650 kg/m3
All other types are classed as ‘Other’ and required appropriate test data.
Notes: Paul to change images

## Slide 22: Supporting construction compatibility type /P.F safety seal type
Protected Corridor or Lobby
Classification
E120 (VE i ↔ o)S
C10000
Frame Type
Wall System Type
Flanged
Cast In
Ablative Batt
Plastered In
Cleats In Wall
Reverse Deflection Head
On Wall
Seal Type
EN520 & Mineral Wool
EN520 overboard
Test Specific Batt & Mastic
Test Specific Wall Kit
EN520 Aperture Framed
Vertical Symmetrical Flexible – EN520
Vertical or Horizontal Rigid – Concrete/ Block > 650 kg/m3
Aperture Framing & Passive Seal specific to test arrangement
Gypsum Plaster specific to test
4:1 Sand and Cement
Wall Thickness is specific to test arrangement
Wall Thickness
Check with the damper manufactures DOP and compare with other wall system products DOP to ascertain the thickness for all system components (I.E. Doors, FR Ducts, Flues, Glass Screens, Pipework, Busbar, FR Cable Containment Systems)
All other types of wall or floor are classed as “Other” and require supporting test and classification data.
Notes: Paul to change images

## Slide 23
Protected Corridor or Lobby
Classification
E120 (VE i ↔ o)S
C10000
Frame Type
Wall System Type
Flanged
Cast In
Ablative Batt
Plastered In
Cleats In Wall
Reverse Deflection Head
On Wall
Seal Type
EN520 & Mineral Wool
EN520 overboard
Test Specific Batt & Mastic
Test Specific Wall Kit
EN520 Aperture Framed
Vertical Symmetrical Flexible – EN520
Vertical or Horizontal Rigid – Concrete/ Block > 650 kg/m3
Aperture Framing & Passive Seal specific to test arrangement
Gypsum Plaster specific to test
4:1 Sand and Cement
Wall Thickness is specific to test arrangement
Wall Thickness
Check with the damper manufactures DOP and compare with other wall system products DOP to ascertain the thickness for all system components (I.E. Doors, FR Ducts, Flues, Glass Screens, Pipework, Busbar, FR Cable Containment Systems)
All other types of wall or floor are classed as “Other” and require supporting test and classification data.
Supporting construction compatibility type /P.F safety seal type
Notes: Paul to change images

## Slide 24: The Process required for descriptive Fire Dampers
The installation/maintenance access types.
Establish the Passive Fire seal installation & maintenance access and sequence
Add the Passive Fire Seals BWIC information to the seal register
Confirm spatial coordination of systems using prescriptive products
Example:
Refuge in protected corridor with supply air and extract.
Supporting construction compatibility type /P.F safety seal type
Gateway points
Notes: Paul to change images

## Slide 25: The installation/maintenance access types
Protected Corridor or Lobby
Classification
E120 (VE i ↔ o)S
C10000
Flanged
Installation Requirements
Damper
Frame
Wall Type
Symmetrical Flexible – EN520
EN520 & Mineral Wool
Seal Type
Wall System Thickness
122mm (example determination)
Wall
Position
Ve – Vertical
Duct
500mm-600mm access
Seal Access
Duct
500mm to form break away joint
Break Away Joints
500mm to form break away joint
500mm-600mm access
Blade types DP (AD: L)
Opposed
* Distance from slab 75mm min or distance as required by the fire wall for its tested requirements
*
*
*
500mm-600mm access
Notes: Paul to change images

## Slide 26: Descriptive Complete – Fire Damper
Protected Corridor or Lobby
Classification
E120 (VE i ↔ o)S
C10000
Flanged
Damper
Frame
Wall Type
Symmetrical Flexible – EN520
EN520 & Mineral Wool
Seal Type
Wall System Thickness
122mm (example determination)
Wall
Position
Ve – Vertical
Blade types DP (AD: L)
Opposed
Classification
E | 120 | VE | i ↔ o | S | C10000
Notes: Paul to change images

## Slide 27
Scheduling of products – Fire Dampers

## Slide 28: Further Reading
Fire Stopping of Service Penetrations
Best Practice in Design and Installation
Free Download from ASFP, FIS, BSRIA and BESA
ASFP Grey Book (2nd Edition)
Volume 1:
Fire dampers (European standards) E (integrity) & ES (integrity and leakage) classified
Available for download from ASFP
DW 145
For the installation of fire and smoke dampers.
Available for download from BESA
NAAD22
Fire Dampers
Available for download from NAADUK

## Slide 29
Disclaimer The Passive Fire Knowledge Group (PFKG) is a not-for-profit collaborative group of specialists working within various fields of passive fire protection. The aim of the PFKG is to promote passive fire protection guidance and best practice and improve the delivery of well designed, specified and installed passive fire protection. Information is produced by subject matter experts, peer reviewed and signed off by the PFKG Governance group before publication. All information contained on the PFKG website and its publications, video libraries, and training resources is for general information and guidance only and does not purport to be and should not be considered as a professional or legal advice. Whilst all reasonable steps have been taken to ensure that the information contained on the PFKG website and within its publications is correct to the best of our knowledge, complete accuracy cannot be guaranteed, and the information contained within it may be incomplete or may be due for updates or changes. Accordingly, the PFKG, its subject matter experts, and the co-publishers make no warranties or representations of any kind as to the content or accuracy of its information and, to the maximum extent permitted by law, accept no liability whatsoever for the same including, without limit, any technical, editorial, typographical or other errors or omissions in or misinterpretations of the information provided on their website, and for direct, indirect or consequential loss, business interruption, loss of business opportunity, loss of profits, production, contracts, goodwill or anticipated savings.
Any person making use of the PFKG’s information does so at his or her own risk and it is recommended that they seek professional advice whenever appropriate. In no event will the PFKG, its subject matter experts, and its co-publishers be liable to anyone for any decision made or action taken in reliance on the information published on the PFKG website or for any consequential, special, or similar damages, even if advised of the possibility of such damages.